## Private Supply Scope-2
Private EVCS Supply Scope-2
Nesco Gate No. 3 _60KW Electrical BOM BOM No : TCZL/2023/DE/04/NH(VAP)/34
Sr. No. | Item Code | Item Description | Purpose | Make | Qty | UoM
1.01 |  | Supply of Outdoor of 200A Ceramic fuse with Box Enclosure | Between Transformer to Meter | Based On Discom Approved | 1 | Set
1.02 |  | Supply of 125A, 4P,36KA Thermal Magnetic with O/L & S/C Protection MCCB With Enclosure (Minimum IP54) With MS Channel 50x50x6 MM channel stand | Between Meter to ACDB | L&T/ Schider/Simens/ABB | 1 | Nos
2.01 |  | Supply of 1.1kV L.T. CABLE 1 Runs of 3.5C X150Sq mm Aluminium armoured XLPE cable. | MCCB to ACDB | Polycab | 200 | Meter
2.02 |  | Supply of Double compression Nickle Plated brass cable glands (50 MM) for 1.1kV Grade ,3.5C X150 Sq.mm Al Armoured XLPE Cable | MCCB to ACDB | Dowells/Comet | 3 | Nos
2.03 |  | Supply of Aluminium Aluminium Barrel Type lugs with M-8 Hall Dia for 1.1kV Grade ,3.5C X 150 Sq.mm Al Armoured XLPE Cable | MCCB to ACDB | Dowells/Comet | 12 | Nos
2.04 |  | Supply of 1.1kV L.T. CABLE 1 Runs of 4C X 95 Sq mm copper unarmoured cable. | ACDB To Charger | Polycab | 12 | Meter
2.05 |  | Supply of Single compression Nickle Plated Brass cable glands (38-42 MM) 1.1kV Grade ,4C X 95 Sq mm copper Unarmoured XLPE Cable | ACDB To Charger | Dowells/Comet | 2 | Nos
2.06 |  | Supply of Copper Ring Type lugs with M-8 Hall Dia for 1.1kV Grade ,4C X 95 Sq mm copper Unarmoured XLPE Cable | ACDB To Charger | Dowells/Comet | 8 | Nos
2.07 |  | Supply of Single compression cable glands 10 Sq.mm Copper Unarmoured FRLS Cable | Canopy to ACDB | Dowells/Comet | 2 | Nos.
2.08 |  | Supply of Pin Type lugs for 2C X2.5 Sq.mm Copper Unarmoured FRLS Cable | Canopy to ACDB | Dowells/Comet | 2 | Nos.
3.01 |  | Supply of Copper bonded Steel rod of 3 Meter length,17.2mm dia having 250 micron copper coating, copper bonded rod UL certified and CPRI tested having a bus exothermic welded busbar (150x25x6mm) | Charger -01 ACDB -01 | As per Approved of Particular Discom/Utility | 2 | JMV
3.02 |  | Earth Enhancement Compound Chemical Bag 25kg | Earthing Compound | As per Approved of Particular Discom/Utility | 4 | Bag
3.03 |  | Earth-Pit Chamber(FRP) with Cover (FRP) Having Dimension of 350X350X350mm_The identification number shall be provided both inside and outside. | Charger -01 ACDB -01 | As per Approved of Particular Discom/Utility | 2 | Nos.
3.04 |  | Supply of 25X6 MM GI Strip | For Charger and ACDB Earthing | ISI marked | 200 | Mtrs
3.05 |  | Supply of 1C x 35 sq.mm Copper flexible cable green colored | For Charger and ACDB Earthing | Polycab | 10 | Mtrs
3.06 |  | Supply of 35 Sqmm copper Lugs with Hall Dia M-8 for 1C x 35 sq.mm for green color Cable | For Charger and ACDB Earthing | Dowells/Comet | 4 | Nos.
3.07 |  | Supply of 1C x 16 sq.mm Copper flexible cable green color | Interconncetion of Both Earthing | Polycab | 10 | Mtrs
3.08 |  | Supply of 16 Sqmm copper Lugs with Hall Dia M-8 for 1C x16 sq.mm for Copper cable green color | Interconncetion of Both Earthing & Canopy earthing | Dowells/Comet | 2 | Nos.
4.01 |  | 95 mm_Outer Diameter DWC Pipe | For underground cabeling | D-Rex/Finolex | 50 | Mtrs
4.02 |  | 95 mm_Outer Diameter UPVC Pipe | For Foundation grouting and DB to Charger underground | D-Rex/Finolex | 10 | Mtrs
4.03 |  | Perforated Cable Tray, 50mm X 150 mm, 2 mm Thickness,with cover and ceiling U support with laying charges (As per Approved drwg. / Issued for construction drwg) Approx. | From transformer to ACDB |  | 140 | Mtrs
4.04 |  | Connectors/Coupling_95 mm OD DWC Pipe (45°/90° as per requirements) |  | D-Rex/Finolex | 10 | Nos
4.05 |  | 40 mm_Outer Diameter UPVC Pipe |  |  | 8 | Mtrs
4.06 |  | Connectors/Coupling_40 mm OD UPVC Pipe (45° or 90° as per requirements) | From DB panel to Charger | D-Rex/Finolex | 2 | Nos
4.07 |  | 25 mm_Outer Diameter UPVC Pipe | From DB panel to Charger | D-Rex/Finolex | 15 | Mtrs
4.08 |  | Connectors/Coupling/T _25 mm OD DWC Pipe (45° or 90° as per requirements) | From DB panel to Charger | D-Rex/Finolex | 4 | Nos
5.01 |  | Supply of Stored Pressure (250 kgf/Sq.cm) Type CO2 Fire Extinguiser, 4.5 Kg Capacity, Suitable for Class B & C & Electrically Energised Fire, As per IS 15683:2018, Fire Rating 21B_With Annexure-IV | Fire Safety |  | 1 | Nos
5.02 |  | Rubber Mat in front of Charger(1 Mtr. X 1 Mtr.) and Db panel (1Mtr X 0.5 Mtr.) Thickness : 3 mm | Electrical safety | ISI marked | 1.5 | Sq. Mtr.
6.01 |  | Supply of PVC Tape RYBG |  | Pidilite | 1 | Set
6.02 |  | M12 Anchor Fastener -100 mm/ 150mm |  |  | 8 | Nos.
6.03 |  | Supply of Polyurethane Expansion PU Foam Spray with Gun (500 ml) |  | Pidilite | 1 | Nos.